Results from BSRIA Test Data to BSEN 442-1

@ Flow rate: 56g/sec

All test data based on powder coated white finish RAL 9010 to BS-EN 12206-1.

Urban LT Profile (150mm/6" x 20mm)
Weight: 1.35kg/m

| Boiler Temp | Watts/m | BTU/m | BTU/ft |
| --- | --- | --- | --- |
| Dt50 (72°C flow) | 148.50 | 506 | 153 |
| 40°C | 46 | 157 | 45 |
| 45°C | 59 | 201 | 60 |
| 50°C | 73 | 249 | 75 |
| 55°C | 88 | 300 | 91 |
| 60°C | 104 | 355 | 106 |
| 70°C | 142 | 484 | 139 |
| 75°C | 159 | 542 | 164 |

Classic Torus TS Profile (150mm/6" x 20mm)
Weight: 1.35kg/m

| Boiler Temp | Watts/m | BTU/m | BTU/ft |
| --- | --- | --- | --- |
| Dt50 (72°C flow) | 150 | 512 | 155 |
| 40°C | 47 | 160 | 48 |
| 45°C | 60 | 205 | 62 |
| 50°C | 74 | 252 | 76 |
| 55°C | 89 | 304 | 92 |
| 60°C | 105 | 358 | 108 |
| 70°C | 144 | 491 | 149 |
| 75°C | 160 | 546 | 165 |

Regency OG Profile (200mm/8" x 20mm)
Weight: 1.65kg/m

| Boiler Temp | Watts/m | BTU/m | BTU/ft |
| --- | --- | --- | --- |
| Dt50 (72°C flow) | 170.80 | 583 | 177 |
| 40°C | 52.90 | 180 | 55 |
| 45°C | 67.90 | 231 | 70 |
| 50°C | 84.00 | 287 | 87 |
| 55°C | 101.20 | 345 | 105 |
| 60°C | 119.60 | 408 | 124 |
| 70°C | 163.30 | 557 | 169 |
| 75°C | 182.90 | 624 | 189 |

Deco Profile (115mm/5" x 20mm)
Estimated subject to BSRIA test
Weight: 1.1kg/m

| Boiler Temp | Watts/m | BTU/m | BTU/ft |
| --- | --- | --- | --- |
| Dt50 (72°C flow) | 131.20 | 448 | 136 |
| 40°C | 41.40 | 141 | 43 |
| 45°C | 53.10 | 181 | 55 |
| 50°C | 65.70 | 224 | 68 |
| 55°C | 79.20 | 270 | 82 |
| 60°C | 93.60 | 319 | 97 |
| 70°C | 127.80 | 436 | 132 |
| 75°C | 143.10 | 488 | 148 |

“DiscreteHeat recommends an allowance of up to 3% to these outputs on exterior walls to allow for back losses. Further precautions may be required depending on the age and/or nature of the construction of the building – please contact DiscreteHeat for advice.”

| ThermaSkirt ® Material: Aluminium & Polymer Alloy Thermal Conductivity: 236w/m2/K Water Content 0.49l per m Paint Finish: to BS EN 12206-1 Foil Finish (where applied) Renolit MBAS 0.15mm Corrosion Resistance: Excellent Oxygen Permeability: 0 (Negligible) |  | Connectors Material: Non Hygroscopic Engineering grade polypropylene / Nylon mix Oxygen Permeability: 0 (Negligible) O Ring: Balanced Twin Shore Viton & Silicon Mix Maximum Operating Pressure: 10bar (150psi) Maximum Op. Temperature: (Greater than or Equal to) 130°C |
| --- | --- | --- |
| Valves & Return Manifold Material: Non Hygroscopic Engineering grade polypropylene / Nylon mix Oxygen Permeability: 0 (Negligible) O Ring: Balanced Twin Shore Viton & Silicon Mix Maximum Operating Pressure: 10bar (150psi) Maximum Op. Temperature: (Greater than or Equal to) 130°C |  | Connector Clips, Brackets & Fixtures Punch pressed 306 Stainless Steel Mounting Brackets (LT, TS & OG) High Temperature Resistant Graphite Nylon Covers & Corners Ultra-stable temperature resistant ABS & UPVC Foil Finish (where applied) Renolit MBAS 0.15mm |